## 120KW 6BTAA5.9-G2
XIAMEN AOSIF ENGINEERING LTD.
Add: No.60 Jinying Road, Jimei district, Xiamen 361022, China
Tel: 86-592-2620131 Fax: 86-592-2620112 Email: nancy@aosif.com.cn
Http://www.aosif.com
Powered by
Cummins 6BTAA5.9-G2
150KVA at 60Hz, 220V
General feature:
♦ Assembled by Cummins diesel engine and Leroy Somer alternator.
♦ Three filters as standard, fuel and water separator as optional.
♦ Radiator and fan with safety guard.
♦ Single bearing alternator IP 23, Insulation Class H.
♦ Heavy duty steel as base frame and 8hrs operation base fuel tank.
♦ Automatic control panel and 3 poles circuit breaker, internal cable.
♦ 12V or 24V battery, battery wires.
♦ Battery charger and float battery charger as standard supply scope.
♦ Optional soundproof canopy, ATS, synchronization panel, movable trailers.
Genset Main Technical Data:
Genset Model | [5 empty] | AC165-II
Prime Power(60Hz) | [5 empty] | 120KW / 150KVA
Standby Power(60Hz) | [5 empty] | 132KW / 165KVA
Frequency/Speed | [5 empty] | 60Hz/1800rpm
Standard Voltage | [5 empty] | 380V/220V
Voltage Available | [5 empty] | 400V/230V
Phases | [5 empty] | Three phases, four wires
Manufacturer | [5 empty] | Xiamen AOSIF Engineering LTD.
(1) PRP: Prime Power is available for an unlimited number of annual operating hours in variable load applications, in accordance with ISO8528-1. A 10% overload capability is available for a period of 1 hour within 12-hour period of operation. In accordance with ISO 3046-1. (2) ESP: The Standby Power Rating is applicable for supplying emergency power in variable load applications for up to 200 hours per year in accordance with ISO8528-1. Overload is not allowed.
Cummins Engine Data:
Manufacturer |  |  |  |  | Dongfeng Cummins Engine Co., Ltd.
Model |  |  |  |  | 6BTAA5.9-G2
Engine speed |  |  |  |  | 1800rpm
Engine power
----------------------------Standby power |  |  |  |  | 143kw / 194HP
----------------------Base output power |  |  |  |  | 130kw / 174HP
Air intake way |  |  |  |  | Air-air after-cooled, turbo-charged
Cylinder quantity |  |  |  |  | 6
Bore * Stroke |  |  |  |  | 102*120mm
Displacement |  |  |  |  | 5.9L
Fuel system |  |  |  |  | PB pump _ GAC governor / BYC ASIMCO
Speed-droop |  |  |  |  | 5%
Low idle |  |  |  |  | 750-850 rpm
Piston speed |  |  |  |  | 6.0 m/s
Friction energy output |  |  |  |  | 12.7 kw
Fuel Consumption:
Exhaust system:
Max. back pressure | [5 empty] | 76 mmHg
Diameter of exhaust pipe recommended | [5 empty] | 75mm
Exhaust flow (base output _ standby power) | [5 empty] | 293 _ 324 L/sec
Exhaust temperature (base output _ standby power) | [5 empty] | 481 _ 495 ℃
Air intake system:
Max. air intake resistance
---------Dirty filter | [5 empty] | 635 mmH2O
---------Normal air cleaner and clean filter | [5 empty] | 254 mmH2O
---------Heavy duty cleaner and clean filter | [5 empty] | 381 mmH2O
Diameter of intake pipe recommended | [5 empty] | 100 mm
Air intake flow (base output _ standby power) | [5 empty] | 135 _ 145 L/sec
Lubrication system:
Normal oil pressure range
-----------Low idle | [5 empty] | 207 kPa
-----------Rated speed | [5 empty] | 345 kpa
Max. oil temperature permitted in oil pan | [5 empty] | 121 ℃
Oil pan capacity (Max_ Min) | [5 empty] | 14.2 _ 12.3 L
Lubrication system Min. capacity (oil pan + oil filter) | [5 empty] | 16.3 L
Usage inclining degree permitted (any direction) | [5 empty] | 40 °
Fuel system:
Fuel injection pump model | [5 empty] | PB pump _ GAC governor / BYC ASIMCO
Max. fuel input resistance of transfer pump | [5 empty] | 102 mmHg
Max. overflow fuel resistance at overflow pipe of injector | [5 empty] | 254 mmHg
Total fuel overflow amount | [5 empty] | 30 L/h
Cooling system:
Coolant capacity – engine only | [5 empty] | 9.9L
Max. coolant cycling resistance exterior engine | [5 empty] | 28 kPa
Thermostat adjusting temperature (range) | [5 empty] | 82_95 ℃
Min. opening pressure of radiator cap | [5 empty] | 69 kPa
Max. coolant temperature permitted (standby power_ Base output power) | [5 empty] | 104 _ 100 ℃
Engine coolant flow (base output _ standby power) | [5 empty] | 2.0 _ 2.0 L/sec
Coolant energy output (base output _ standby power) | [5 empty] | 45 _ 50 kW
Electric system:
Starter | [5 empty] | 12V |  |  |  | 24V
Battery charging system | [5 empty] | 63A |  |  |  | 40A
Max. starting circuit resistance | [5 empty] | 0.00075 Ω |  |  |  | 0.002 Ω
Min. battery capacity_ -12℃(CCA: cold cranking Ampere) | [5 empty] | 800 CCA |  |  |  | 400 CCA
ALTERNATOR Specifications:
Manufacturer | [5 empty] | Leroy-somer Electro-technique (Fuzhou) Company Ltd.
Model | [5 empty] | LSA44.2 M95
Output power | [5 empty] | 124KW
AVR model | [5 empty] | R250
Number of phase | [5 empty] | 3
Power factor (Cos Phi) | [5 empty] | 0.8
Altitude | [5 empty] | ≤ 1000 m
Overspeed | [5 empty] | 2250RPM
Number of Pole | [5 empty] | 4
Exciter type | [5 empty] | Shunt
Insulation class | [5 empty] | H
Voltage regulation | [5 empty] | ±0.5%
Sustained short circuit current | [5 empty] | 300% (3 IN) : 10s
Total harmonics (TGH/THC) | [5 empty] | < 4 %
Wave form : NEMA = TIF | [5 empty] | < 50
Wave form : I.E.C. = THF | [5 empty] | < 2%
Bearing | [5 empty] | single
Coupling | [5 empty] | Direct
ALTERNATOR GENERAL DATA：
♦ Operate either 60Hz or 60Hz. | [5 empty] | ♦Stator grease insulation covered
♦ Standard enclosure IP23, but IP44, IP55 for option | [5 empty] | ♦Rotator and excitation high polymer
♦ Insulation class H. | [5 empty] | ♦ Resist the corruption oil and acid
♦ Shunt excitataion systems. | [5 empty] | ♦Rotator balance is in accordance with BS5625
♦ AREP or PMG system for options. | [5 empty] | standard 12.5
♦ Automatic voltage regulator | [5 empty] | ♦High-quality lubrication sealed long-time bearing
♦ Single bearing alternator | [5 empty] | ♦Rotator silicon steel close tight
OTHER ALTERNATOR DATA：
REACTANCES (%) - TIME CONSTANTS (ms): CLASS : H / 400 V
Kcc |  | Short-circuit ratio | [8 empty] | 0.31
Xd |  | Direct axis synchronous reactance unsaturated | [8 empty] | 392
Xq |  | Quadrature axis synchronous reactance unsaturated | [8 empty] | 235
T'do |  | Open circuit time constant | [8 empty] | 2734
X'd |  | Direct axis transient reactance saturated | [8 empty] | 14.3
T'd |  | Short circuit transient time constant | [8 empty] | 100
X"d |  | Direct axis subtransient reactance saturated | [8 empty] | 8.6
T"d |  | Subtransient time constant | [8 empty] | 10
X"q |  | Quadrature axis subtransient reactance saturated | [8 empty] | 10.3
Xo |  | Zero sequence reactance unsaturated | [8 empty] | 0.9
X2 |  | Negative sequence reactance saturated | [8 empty] | 9.5
Ta |  | Armature time constant | [8 empty] | 15
OTHER DATA - CLASS : H / 400 V
io |  | No load excitation current (A) (SHUNT/AREP) | [8 empty] | 0,5/1
ic |  | Full load excitation current (A) (SHUNT/AREP) | [8 empty] | 2.1/4.2
uc |  | Full load excitation voltage (V) (SHUNT/AREP) | [8 empty] | 38/19
ms |  | Recovery time(∆U =20 % trans.) | [8 empty] | 500
Kva(Shunt) |  | Motor start. (∆U = 20% sust.) or (∆U = 50% Transient) | [8 empty] | 246.4
Kva(AREP) |  | Motor start. (∆U = 20% sust.) or (∆U = 50% Transient) | [8 empty] | 287.3
% |  | Transient dip (rated step load) SHUNT / PF : 0,8 LAG | [8 empty] | 17.5
% |  | Transient dip (rated step load) AREP / PF : 0,8 LAG | [8 empty] | 14.4
W |  | No load losses | [8 empty] | 1970
AOSIF Circuit breaker specification:
| Manufacturer | [5 empty] | Delixi group
| Brand | [5 empty] | Delixi
| Model | [5 empty] | DZ20Y-630/250 3300
| Capacity | [5 empty] | 250amp
| Voltage | [5 empty] | 380V
AOSIF Starting Battery specification:
| Battery Voltage | [5 empty] | 12V
| Battery Capacity | [5 empty] | 120aH
| Quantity | [5 empty] | 2 pcs
| Battery type | [5 empty] | lead acid, chargeable
Control system:
Deepsea 6020
Auto start and stop control panel
Deepsea 6020 is an auto mains failure controller for single generator, it can monitor and protect the generator working all the time. it has a LCD display which clearly shows the status of the engine. this controller include seven inputs and six outputs. This controller can also be programmed using the frong panel or by using DSE configuration Suite PC software. Parameters: This controller can provide Generator frequency, Under/over speed, Generator volts, Generator current, Engine oil pressure, Engine coolant temperature, Flexible fuel level, Hours run counter, Battery volts, Fail to start/stop, Emergency Stop. Failed to reach loading voltage/frequency, Charge fail, Loss of magnetic pick-up signal, Low DC voltage, CAN diagnostics and CAN fail/error, Mains volts 3 phase, Mains frequency, AMF indications Protection: ♦Low Oil Pressure ♦High water Temperature ♦High voltage and low voltage ♦Overspeed |  |  | ♦Volt adjuster and frequency adjuster. ♦Emergency stop ♦Fail to start Features: ♦Protection: Automatic start/stop, load transfer and alarming of generator; ♦ CAN and magnetic pick-up versions. ♦PC and front panel configurable ♦4 digital inputs and 3 analogue inputs. ♦6 outputs(4 configurable on magnetic pick-up, 6 configurable on Canbus version). ♦3 phase generator and mains voltage monitoring. ♦remote start on or off load. ♦advanced metering capability. ♦test button. ♦protected solid state outputs. ♦transfer between mains and generator power. ♦user-friendly set-up and button layout. ♦multiple engine parameters are monitored simultaneously. ♦module can be configured to suit individual applications. ♦IP 65 rating offers advanced resistance to water ingress when gasket is fitted.
① Power switch
② Lamp switch
③ Power indicator
④ Operation buttons
⑤ LCD display
Open type
Silent type
AOSIF Soundproof Enclosure Specification:
AOSIF silent generator is designed by professional acoustic engineers based on 11 years experience, Now we can make the noise of the generator less than 80-85dB(A) at 1m, or 70~75dB(A) at 7m, 60~65dB(A) at 15m.
★ multi-way air intake and exhaust guarantee the power performance of the generator. ★large-scale impedance combined type silencer effectively reduce noise of the generator. ★ internal high performance rubber damper and flexible materials reduce vibration. ★ Base mounted fuel tank supports the generator running for 8 hours.
★Transparent viewing window make the control panel clear at a glance. ★Emergency stop button mounted on the canopy exterior for urgency. ★Cooling fluid injection hole is kept on the ceiling crust. ★Pipe of lube oil and cooling fluid is mounted on the bottom of generator for easy let. ★Fuel fill and battery can easy be accessed by lockable door. ★Cooling fan and battery are fully guarded. ★Heat insulation of exhaust smoke system inside the canopy. ★Forkman slot is for choice. ★Lifting ear is mounted in the base frame.
★ Cold steel materials of the canopy. ★ Best powder paint. ★ Zinc plated and Corrosion resistance. ★ Elegant appearance and reliable quality. ★ Stainless steel locks and hinges. ★ Access to all weather conditions. ★ Fireproof, waterproof and dustproof. ★ High quality soundproof materials could efficiently reduce noise. ★ Big base fuel tank in the frame guarantee sufficient diesel supply. ★ 180° revolvable and disassemble door for easy maintenance. ★ Concave lockable access door for easy operation and indefectible. ★ Lights inside of the canopy for maintenance.
Weight and Dimensions
1.Open Version: |  |  |  |  | 2. Soundproof Version:
Supply scope
1.Standard supply scope:
⑦ Exhaust silencer
⑧ Starting battery
⑨ Float battery charger
|  |  |  | ① Auto Control Panel |  |  |  | ④ Base Frame
|  |  |  | ② Main Ciruit Breaker |  |  |  | ⑤ Filter
|  |  |  | ③ Cooling Radiator |  |  |  | ⑥ Starting Motor
⑩ Bellow
2. Optional supply scope:
Our Sales Promises
★AOSIF Engineering provides a full line of brand new and high quality products. Each and every unit is strictly factory tested before shipment. ★Quality Warranty is according to our standard conditions: 12 months from BL date or 1,000 running hours, whichever comes first. ★Service and parts are available from XIAMEN AOSIF Engineering Ltd. or distributors in your location. ★All the products from Xiamen AOSIF Engineering Ltd. is CE marked.
Specifications are subject to change without notice.
©XIAMEN AOSIF ENGINEERING LTD. Add: No.60 Jinying Road, Jimei district, Xiamen 361022, China Tel: 86-592-2620131 Fax: 86-592-2620112 Email: nancy@aosif.com.cn Http://www.aosif.com
Cummins Power Generator
AOSIF Cummins Series
AC165-II Technical Data
① ATS
⑩ Trailer &
Silent Canopy
⑥ Synchronization System
④ External daily fuel tank
Open Type (Standard Configuration)
Overall Size: 2210×785 ×1405mm(L*W*H)
Weight: 1207kg
Soundproof Type
Overall size: 3100× 1050×1830mm(L*W*H)
Weight: 1687kg
⑧ Elec.coolant Heater
③ Auto Fuel Pump
⑨ Oil drain Pump
150KVA/120KW
①
④
⑤
③
⑤ ABB Breaker
⑦ Lub oil heater
⑥
② fuel and water separator
⑤
②
kw
①
②
③
④
⑤